## Sheet 1
CHP PROJECT ANALYSIS DECISION SUPPORT MODEL INPUT QUESTIONS
Title of Project |  | PhD (2) Ltd -CHP study
Date of Submission |  | 2002-09-01
True =1, False=0
Type of Building |  |  | Office | 0 | 0
|  |  | Factory | 1 | 60
|  |  | Hospital | 0 | 0
|  |  | Leisure | 0 | 0
|  |  | Sewerage | 0 | 0
|  |  | Hotels | 0 | 0
60
Area of Building (Sq M)
|  |  |  | True=1, False=0 | 20 Yr Ave D/D
Regional location of Building |  |  | South East | 1 | 320
|  |  | Southern | 0 | 0
|  |  | South West | 0 | 0
|  |  | Thames Valley | 0 | 0
|  |  | Severn Valley | 0 | 0
|  |  | Midlands | 0 | 0
|  |  | West Pennines | 0 | 0
|  |  | North West | 0 | 0
|  |  | Borders | 0 | 0
|  |  | North East | 0 | 0
|  |  | East Pennines | 0 | 0
|  |  | East Anglia | 0 | 0
|  |  | West Scotland | 0 | 0
|  |  | East Scotland | 0 | 0
|  |  | N E Scotland | 0 | 0
|  |  | N W Scotland | 0 | 0
|  |  | Wales | 0 | 0
|  |  | Northern Ireland | 0 | 0
320
Primary Fuel |  | Natural Gas | Solid Fuels | Oil
|  | 1 | 0 | 0
|  | 50 | 0 | 0 | 50
Existing boiler Details |  | Space Heating | Capacity (Mwh) | Age (Yrs) | Mtce Cost/Yr (£)
|  | 1 | 640 | 15 | 2250
|  | 2 |  | n/a | 660
|  | 3 |  | n/a
|  | Hot Water |  | 12 | 400
Total |  |  | 640 | 15 | 3310
True=1, false=0
CHP Requirement |  |  | Boiler Replacement | 0 | 0
|  |  | New Capacity | 1 | 60
60
True=1, false=0
Space Availability |  |  | Yes | 0 | 0
|  |  | New Location | 1 | 60
60
[5 empty] | % | En.Factor
Energy Efficiency Measures |  |  | Building Insulation | Part | 1 | 1.2
|  |  |  | Full | 100%
|  |  | Double Glazing | Part | 0 | 1.05
|  |  |  | Full | 100%
|  |  | Pipe Insulation | Part | 0 | 1.1
|  |  |  | Full | 100%
|  |  | Low Energy Lights | Part | 0% | 1.05
|  |  |  | Full | 100%
|  |  | Energy Mgmt System | Yes | 0% | 1.15
|  |  |  | No |  | 1
True=1,False=0
Key Staff |  |  | Technical Manager | 1 | 50
True=1,False=0
Maintenance Capability |  | 1 | Own Staff | 1 | 50
|  | 2 | Specialist Mtce Staff | 0 | 0
|  | 3 | Manufacturer | 0 | 0
50
Average Fuel Prices |  |  |  | P/kWh
|  |  | Gas | 0.84
|  |  | Oil | 6
|  |  | Electricity | 4.4
Utility Consumption |  | Primary Fuel (mWh) | Monthly Cost (£) | Electricity (mWh) | Monthly Cost (£)
| January | 121 | 1016.4 | 10 | 440
| February | 101 | 848.4 | 17 | 748
| March | 90 | 756 | 9 | 396
| April | 23 | 193.2 | 7 | 308
| May | 17 | 142.8 | 5 | 220
| June | 22 | 184.8 | 4 | 176
| July | 1 | 8.4 | 3 | 132
| August | 1 | 8.4 | 8 | 352
| September | 20 | 168 | 12 | 528
| October | 17 | 142.8 | 7 | 308
| November | 85 | 714 | 26 | 1144
| December | 102 | 856.8 | 17 | 748
Total |  | 600 | 5040 | 125 | 5500

## Sheet2
NPV
Client: PhD (2) |  |  | Years | Exp | Inc
CHP Decision Support Indicators |  |  | 1 | 44544 | 3463.0848 | -41080.9152
Energy Ratio | 0.33368 |  | 2 | 0 | 3463.0848 | 3463.0848
Carbon Dioxide Emissions/yr (T) | 224.75 |  | 3 | 0 | 3463.0848 | 3463.0848
Annual Energy Consumption (mWh) | 725 |  | 4 | 0 | 3463.0848 | 3463.0848
Annual Energy Bill after CHP | 7076.9152 |  | 5 | 0 | 3463.0848 | 3463.0848
Value of energy Savings per yr (£) | 3463.0848 |  | 6 | 0 | 3463.0848 | 3463.0848
Energy Savings per yr (kWh) | 241920 |  | 7 | 0 | 3463.0848 | 3463.0848
Carbon Dioxide Savings/yr (T) | 323.6352 |  | 8 | 0 | 3463.0848 | 3463.0848
Budget Installed cost of CHP( £) | 44544 |  | 9 | 0 | 3463.0848 | 3463.0848
Simple Payback Period (yrs) | 12.8625 |  | 10 | 4454.4 | 3463.0848 | -991.3152
Area of Building (M2) | 50000 |  | 11 | 0 | 3463.0848 | 3463.0848
NPV over 20 yr life | -15338.3095 |  | 12 | 0 | 3463.0848 | 3463.0848
Energy Cost Index (ECI) (£/M2) | 0.14154 |  | 13 | 0 | 3463.0848 | 3463.0848
Energy Use Index (EUI) (kWh/M2) | 14.5 |  | 14 | 0 | 3463.0848 | 3463.0848
Carbon Saving Index (CEI) (T/M2) | 6.4727 |  | 15 | 0 | 3463.0848 | 3463.0848
Financial Saving Index (£/kWh) | -0.063402 |  | 26 | 0 | 3463.0848 | 3463.0848
Investment Ratio | -0.34434 |  | 17 | 0 | 3463.0848 | 3463.0848
Emissions Ratio | 1.44 |  | 18 | 0 | 3463.0848 | 3463.0848
CHPQI ( Quality Index ) | 115.6897 |  | 19 | 0 | 3463.0848 | 3463.0848
Decision Ratio | -19.1414 |  | 20 | 0 | 3463.0848 | 3463.0848 | -15338.3095
| -19.1414 |  |  | 48998.4 | 69261.696
Decision Support Indicator | 0
INDICATOR CODES
BAD | 1 |  | 0 | 0 | 0 | 0 | 0
MARGINAL | 2 |  | 0 | 0 | 0 | 0 | 0 | 0
GOOD | 3
VERY GOOD | 4
EXCELLENT | 5
| DR = | EmR*EnR*IR*CHPQI

## Sheet 3
CHP Feasibility/Appraial
Client: PhD (2) Ltd |  | Projected Annual Energy Consm (Mwh) & Cost (inc.Climate Change Levy)
|  |  | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | Totals | Cost
|  | Gas | 23 | 17 | 22 | 1 | 1 | 20 | 17 | 85 | 102 | 121 | 101 | 90 | 600 | 5040 | [5 empty] | 22.5
ASSUMPTIONS:- |  | Elect | 7 | 5 | 4 | 3 | 8 | 12 | 7 | 26 | 17 | 10 | 17 | 9 | 125 | 5500 | [5 empty] | 8.5
CHP Plant Electrical Output | 32 | KWe
Heat Output | 54 | KWth
Fuel Input | 116 | KW
Electricity Price (inc. 0.43p CCL) | 4.4 | p/kWh | [14 empty] | 54000 | 725
Gas Price (inc.0.15p CCL+0.15 uplift) | 0.84 | p/kWh | [14 empty] | 57000
Boiler Efficiency | 75% | [15 empty] | 61000 |  | Conversion | carbon factor | conversion
CHP Maintenance charge | 1.1 | p/kWhe | [14 empty] | 68000 |  | Factors | kgC/kWh | to gas equiv.
Equivalent full load | 490 | Hrs/mth | [14 empty] | 62000 |  | Electricity | 0.79 | 2.264
ANALYSIS:- | [16 empty] | 43000 |  | Gas | 0.21 | 1
Electricity Displaced | 1.408 | £/hr | [14 empty] | 44000 |  | Oil | 0.29 | 1.377
Boiler fuel Displaced | 0.6048 | £/hr | [14 empty] | 77000 |  | Coal | 0.29 | 1.585
Total Savings | 2.0128 | £/hr | [14 empty] | 83000
CHP Fuel input | 1.0718 | £/hr | [14 empty] | 79000
CHP Maintenace | 0.352 | £/hr | [14 empty] | 67000
Total Cost | 1.4238 | £/hr | [14 empty] | 43000 |  | Elec Carbon Prod (T) |  | 98.75
NET CHP BENEFIT | 0.58896 | £/hr | [14 empty] | 738000 |  | Gas Carbon Prod (T) |  | 126
Carbon Dioxide Emissions (T/yr) | 224.75 | [17 empty] | Total Carbon Prod |  | 224.75
Annual Energy Bill 2001/2002 | 10540
Annual Energy Bill after CHP | 7076.9152 |  | SEP: CHP; OCT: GRID; DEC: CHP; JAN: BOILERS
Value of energy Savings per yr | 3463.0848 |  | SEP: 1.3067; OCT: 5.6933; NOV: APR; DEC: 2.205; JAN: 20.795
Energy Savings per yr | 241920 | Kwhr | SEP: 1.3067; OCT: 3.6933; NOV: MAY; DEC: 2.205; JAN: 14.795
Carbon Dioxide Savings/yr | 323.6352 | Tonnes | SEP: 1.3067; OCT: 2.6933; NOV: JUN; DEC: 2.205; JAN: 19.795
Budget Installed cost of CHP £ | 44544 |  | SEP: 1.3067; OCT: 1.6933; NOV: JUL; DEC: 2.205; JAN: -1.205
Payback Period | 12.8625 | Years | SEP: 1.3067; OCT: 6.6933; NOV: AUG; DEC: 2.205; JAN: -1.205
CHPQI ( Quality Index ) | 115.6897 |  | SEP: 1.3067; OCT: 10.6933; NOV: SEP; DEC: 2.205; JAN: 17.795
Exemption from CCL | QI > 100 |  | SEP: 1.3067; OCT: 5.6933; NOV: OCT; DEC: 2.205; JAN: 14.795
[8 empty] | 1.3067 | 24.6933 | NOV | 2.205 | 82.795
[8 empty] | 1.3067 | 15.6933 | DEC | 2.205 | 99.795
[8 empty] | 1.3067 | 8.6933 | JAN | 2.205 | 118.795
[8 empty] | 1.3067 | 15.6933 | FEB | 2.205 | 98.795
[8 empty] | 1.3067 | 7.6933 | MAR | 2.205 | 87.795
Decision Index | 0
EmR*IR*EnR*CHPQI

## Sheet 4
(kWth) | (kWe) | Input (kW) | Unit cost | CHP Plant Electrical Output | 150 | KWe
54 | 32 | 116 | 928.13 | Heat Output | 210 | KWth | C2
77 | 36 | 135 | 888.9 | Fuel Input | 480 | KW | C3
90 | 48 | 179 | 653.46
118 | 54 | 202 | 629.63 | Equivalent full load | 5880 | Hrs
215 | 95 | 355 | 515.79
226 | 150 | 462 | 386.15
245 | 110 | 405 | 454.55
266 | 165 | 501 | 515.15
280 | 145 | 518 | 427.59
354 | 230 | 679 | 478.3
455 | 220 | 798 | 418.18
475 | 312 | 897 | 400.64
492 | 300 | 865 | 400 | Median Electrical Output | 8.5 | 3.57 | 490
560 | 310 | 1045 | 387.1 | Median Heat Output(kwh) | 22.5 | 19.125 | 490 | 39.0306 | 12.4898
702 | 470 | 1335 | 404.26 | Min Heat output(kw) |  | 51.5204
997 | 660 | 1939 | 454.55 | Min Electrical Output(kw) |  | 7.2857
1120 | 755 | 2175 | 437.09 | [14 empty] | *
1357 | 920 | 2626 | 472.83
[5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Plant Heat Output | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | Plant Heat Output | kWth
|  |  |  | Plant Electrical Output | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | Plant Electrical Output | kWe
|  |  |  | Plant Fuel Input | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | Plant Fuel Input | kW
|  |  |  | unit cost of plant | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | unit cost of plant | £/kWe

## Sheet 5
Conceptual Model -CHP Climate Change Levy Quality Analysis
| CHP 1 | CHP 2
Electricity Output (kw) | 95 | 185
Heat Output (kw) | 150 | 310
|  |  | Conversion | carbon factor | conversion
Electricity Input |  |  | Factors | kgC/kWh | to gas equiv.
Gas Input (Kw) | 310 | 620 | Electricity | 0.79 | 2.264
Running Hours | nil | 2097 | Gas | 0.21 | 1
Annual electrical Output (kw) | Nil | 387945 | Oil | 0.29 | 1.377
Annual Heat Output (Kw) |  | 650070 | Coal | 0.29 | 1.585
Annual Fuel Input (kw) |  | 1300140
Annual Electrical Efficiency % |  | 29.8387
Annual Heat Efficiency % |  | 50
Q I | Nil | 122.1774
Electricity exported to grid (kw) |  | 60115
Electricity imported from Grid |  | 4614
Cost of CC Levy( Elec Export) |  | 258.4945
CC Levy on Gas consumed (£) |  | 2600.28
CC levy on imported electricity(£) |  | 19.8402
Total cost of CC Levies (£) |  | 2878.6147
Value of levy Exemption (£) |  | 2968.3035
Net cost to client (£) | nil | -89.6888
Total costs to client per annum | 0

## Sheet 6
Conceptual Model-Effect of National insurance savings on Climate Change Levy
Annual Employers NI Contributions; Savings After 0.3 % reduction
at different salary levels in a typical organisation
|  |  | At Present |  | Post CC Levy
Average Yearly Salary | Average Monthly Salary | No. of employees | Monthly NIC per Employee | Total Yearly NIC for all Employees | Monthly NIC per Employee | Total Yearly NIC for all Employees | Saving
12500 | 1041.6667 | 5 | 82.5533 | 4953.2 | 80.5233 | 4831.4 | 121.8
15500 | 1291.6667 | 4 | 113.0533 | 5426.56 | 110.2733 | 5293.12 | 133.44
18000 | 1500 | 3 | 138.47 | 4984.92 | 135.065 | 4862.34 | 122.58
20000 | 1666.6667 | 2 | 158.8033 | 3811.28 | 154.8983 | 3717.56 | 93.72
471.54
Notes
The above calculations assume:
1. everyone pays full National Insurance Contributions (NICs)
2. there is no occupational pension scheme
3. 2000/2001 tax year