## Sheet 1
CHP PROJECT ANALYSIS DECISION SUPPORT MODEL INPUT QUESTIONS
Title of Project |  | PhD Ltd-CHP study
Date of Submission |  | 2002-09-01
True =1, False=0
Type of Building |  |  | Office | 0 | 0
|  |  | Factory | 1 | 60
|  |  | Hospital | 0 | 0
|  |  | Leisure | 0 | 0
|  |  | Sewerage | 0 | 0
|  |  | Hotels | 0 | 0
60
Area of Building (Sq M)
|  |  |  | True=1, False=0 | 20 Yr Ave D/D
Regional location of Building |  |  | South East | 1 | 320
|  |  | Southern | 0 | 0
|  |  | South West | 0 | 0
|  |  | Thames Valley | 0 | 0
|  |  | Severn Valley | 0 | 0
|  |  | Midlands | 0 | 0
|  |  | West Pennines | 0 | 0
|  |  | North West | 0 | 0
|  |  | Borders | 0 | 0
|  |  | North East | 0 | 0
|  |  | East Pennines | 0 | 0
|  |  | East Anglia | 0 | 0
|  |  | West Scotland | 0 | 0
|  |  | East Scotland | 0 | 0
|  |  | N E Scotland | 0 | 0
|  |  | N W Scotland | 0 | 0
|  |  | Wales | 0 | 0
|  |  | Northern Ireland | 0 | 0
320
Primary Fuel |  | Natural Gas | Solid Fuels | Oil
|  | 1 | 0 | 0
|  | 50 | 0 | 0 | 50
Existing boiler Details |  | Space Heating | Capacity (Mwh) | Age (Yrs) | Mtce Cost/Yr (£)
|  | 1 | 1873.0667 | 15 | 2250
|  | 2 |  | n/a | 660
|  | 3 |  | n/a
|  | Hot Water |  | 12 | 400
Total |  |  | 1873.0667 | 15 | 3310
True=1, false=0
CHP Requirement |  |  | Boiler Replacement | 0 | 0
|  |  | New Capacity | 1 | 60
60
True=1, false=0
Space Availability |  |  | Yes | 0 | 0
|  |  | New Location | 1 | 60
60
[5 empty] | % | En.Factor
Energy Efficiency Measures |  |  | Building Insulation | Part | 1 | 1.2
|  |  |  | Full | 100%
|  |  | Double Glazing | Part | 0 | 1.05
|  |  |  | Full | 100%
|  |  | Pipe Insulation | Part | 0 | 1.1
|  |  |  | Full | 100%
|  |  | Low Energy Lights | Part | 0% | 1.05
|  |  |  | Full | 100%
|  |  | Energy Mgmt System | Yes | 0% | 1.15
|  |  |  | No |  | 1
True=1,False=0
Key Staff |  |  | Technical Manager | 1 | 50
True=1,False=0
Maintenance Capability |  | 1 | Own Staff | 1 | 50
|  | 2 | Own Mtce Staff | 0 | 0
|  | 3 | Manufacturer | 0 | 0
50
Average Fuel Prices |  |  |  | P/kWh
|  |  | Gas | 0.84
|  |  | Oil | 6
|  |  | Electricity | 4.4
Utility Consumption |  | Primary Fuel (mWh) | Monthly Cost (£) | Electricity (mWh) | Monthly Cost (£)
| January | 363 | 3049.2 | 175 | 7700
| February | 313 | 2629.2 | 170 | 7480
| March | 260 | 2184 | 189 | 8316
| April | 203 | 1705.2 | 147 | 6468
| May | 57 | 478.8 | 147 | 6468
| June | 11 | 92.4 | 132 | 5808
| July | 3 | 25.2 | 136 | 5984
| August | 3 | 25.2 | 96 | 4224
| September | 24 | 201.6 | 142 | 6248
| October | 118 | 991.2 | 145 | 6380
| November | 233 | 1957.2 | 159 | 6996
| December | 168 | 1411.2 | 114 | 5016
Total |  | 1756 | 14750.4 | 1752 | 77088

## Sheet2
NPV
Client: PhD Ltd |  |  | Years | Exp | Inc
CHP Decision Support Indicators |  |  | 1 | 164910 | 31051.3392 | -133858.6608
Energy Ratio | 0.67334 |  | 2 | 0 | 31051.3392 | 31051.3392
Carbon Dioxide Emissions/yr (T) | 1752.84 |  | 3 | 0 | 31051.3392 | 31051.3392
Annual Energy Consumption (mWh) | 3508 |  | 4 | 0 | 31051.3392 | 31051.3392
Annual Energy Bill after CHP | 60787.0608 |  | 5 | 0 | 31051.3392 | 31051.3392
Value of energy Savings per yr (£) | 31051.3392 |  | 6 | 0 | 31051.3392 | 31051.3392
Energy Savings per yr (kWh) | 2362080 |  | 7 | 0 | 31051.3392 | 31051.3392
Carbon Dioxide Savings/yr (T) | 2457.0168 |  | 8 | 0 | 31051.3392 | 31051.3392
Budget Installed cost of CHP( £) | 164910 |  | 9 | 0 | 31051.3392 | 31051.3392
Simple Payback Period (yrs) | 5.3109 |  | 10 | 16491 | 31051.3392 | 14560.3392
Area of Building (M2) | 50000 |  | 11 | 0 | 31051.3392 | 31051.3392
NPV over 20 yr life | 79385.4955 |  | 12 | 0 | 31051.3392 | 31051.3392
Energy Cost Index (ECI) (£/M2) | 1.2157 |  | 13 | 0 | 31051.3392 | 31051.3392
Energy Use Index (EUI) (kWh/M2) | 70.16 |  | 14 | 0 | 31051.3392 | 31051.3392
Carbon Saving Index (CEI) (T/M2) | 49.1403 |  | 15 | 0 | 31051.3392 | 31051.3392
Financial Saving Index (£/kWh) | 0.033608 |  | 26 | 0 | 31051.3392 | 31051.3392
Investment Ratio | 0.48139 |  | 17 | 0 | 31051.3392 | 31051.3392
Emissions Ratio | 1.4017 |  | 18 | 0 | 31051.3392 | 31051.3392
CHPQI ( Quality Index ) | 135.5228 |  | 19 | 0 | 31051.3392 | 31051.3392
Decision Ratio | 61.5754 |  | 20 | 0 | 31051.3392 | 31051.3392 | 79385.4955
| 61.5754 |  |  | 181401 | 621026.784
Decision Support Indicator | 4
INDICATOR CODES
BAD | 1 |  | 0 | 0 | 0 | 1 | 0
MARGINAL | 2 |  | 0 | 0 | 0 | 4 | 0 | 4
GOOD | 3
VERY GOOD | 4
EXCELLENT | 5
| DR = | EmR*EnR*IR*CHPQI

## Sheet 3
CHP Feasibility/Appraial
Client: PhD Ltd |  | Projected Annual Energy Consm (Mwh) & Cost (inc.Climate Change Levy)
|  |  | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | Totals | Cost
|  | Gas | 203 | 57 | 11 | 3 | 3 | 24 | 118 | 233 | 168 | 363 | 313 | 260 | 1756 | 14750.4 | [5 empty] | 143
ASSUMPTIONS:- |  | Elect | 147 | 147 | 132 | 136 | 96 | 142 | 145 | 159 | 114 | 175 | 170 | 189 | 1752 | 77088 | [5 empty] | 146
CHP Plant Electrical Output | 230 | KWe
Heat Output | 354 | KWth
Fuel Input | 679 | KW
Electricity Price (inc. 0.43p CCL) | 4.4 | p/kWh | [14 empty] | 54000 | 3508
Gas Price (inc.0.15p CCL+0.15 uplift) | 0.84 | p/kWh | [14 empty] | 57000
Boiler Efficiency | 75% | [15 empty] | 61000 |  | Conversion | carbon factor | conversion
CHP Maintenance charge | 1.1 | p/kWhe | [14 empty] | 68000 |  | Factors | kgC/kWh | to gas equiv.
Equivalent full load | 490 | Hrs/mth | [14 empty] | 62000 |  | Electricity | 0.79 | 2.264
ANALYSIS:- | [16 empty] | 43000 |  | Gas | 0.21 | 1
Electricity Displaced | 10.12 | £/hr | [14 empty] | 44000 |  | Oil | 0.29 | 1.377
Boiler fuel Displaced | 3.9648 | £/hr | [14 empty] | 77000 |  | Coal | 0.29 | 1.585
Total Savings | 14.0848 | £/hr | [14 empty] | 83000
CHP Fuel input | 6.274 | £/hr | [14 empty] | 79000
CHP Maintenace | 2.53 | £/hr | [14 empty] | 67000
Total Cost | 8.804 | £/hr | [14 empty] | 43000 |  | Elec Carbon Prod (T) |  | 1384.08
NET CHP BENEFIT | 5.2808 | £/hr | [14 empty] | 738000 |  | Gas Carbon Prod (T) |  | 368.76
Carbon Dioxide Emissions (T/yr) | 1752.84 | [17 empty] | Total Carbon Prod |  | 1752.84
Annual Energy Bill 2001/2002 | 91838.4
Annual Energy Bill after CHP | 60787.0608 |  | SEP: CHP; OCT: GRID; DEC: CHP; JAN: BOILERS
Value of energy Savings per yr | 31051.3392 |  | SEP: 9.3917; OCT: 137.6083; NOV: APR; DEC: 14.455; JAN: 188.545
Energy Savings per yr | 2362080 | Kwhr | SEP: 9.3917; OCT: 137.6083; NOV: MAY; DEC: 14.455; JAN: 42.545
Carbon Dioxide Savings/yr | 2457.0168 | Tonnes | SEP: 9.3917; OCT: 122.6083; NOV: JUN; DEC: 14.455; JAN: -3.455
Budget Installed cost of CHP £ | 164910 |  | SEP: 9.3917; OCT: 126.6083; NOV: JUL; DEC: 14.455; JAN: -11.455
Payback Period | 5.3109 | Years | SEP: 9.3917; OCT: 86.6083; NOV: AUG; DEC: 14.455; JAN: -11.455
CHPQI ( Quality Index ) | 135.5228 |  | SEP: 9.3917; OCT: 132.6083; NOV: SEP; DEC: 14.455; JAN: 9.545
Exemption from CCL | QI > 100 |  | SEP: 9.3917; OCT: 135.6083; NOV: OCT; DEC: 14.455; JAN: 103.545
[8 empty] | 9.3917 | 149.6083 | NOV | 14.455 | 218.545
[8 empty] | 9.3917 | 104.6083 | DEC | 14.455 | 153.545
[8 empty] | 9.3917 | 165.6083 | JAN | 14.455 | 348.545
[8 empty] | 9.3917 | 160.6083 | FEB | 14.455 | 298.545
[8 empty] | 9.3917 | 179.6083 | MAR | 14.455 | 245.545
Decision Index | 4
EmR*IR*EnR*CHPQI

## Sheet 4
(kWth) | (kWe) | Input (kW) | Unit cost | CHP Plant Electrical Output | 150 | KWe
54 | 32 | 116 | 928.13 | Heat Output | 210 | KWth | C2
77 | 36 | 135 | 888.9 | Fuel Input | 480 | KW | C3
90 | 48 | 179 | 653.46
118 | 54 | 202 | 629.63 | Equivalent full load | 5880 | Hrs
215 | 95 | 355 | 515.79
226 | 150 | 462 | 386.15
245 | 110 | 405 | 454.55
266 | 165 | 501 | 515.15
280 | 145 | 518 | 427.59
354 | 230 | 679 | 478.3
455 | 220 | 798 | 418.18
475 | 312 | 897 | 400.64
492 | 300 | 865 | 400 | Median Electrical Output | 146 | 61.32 | 490
560 | 310 | 1045 | 387.1 | Median Heat Output(kwh) | 143 | 121.55 | 490 | 248.0612 | 79.3796
702 | 470 | 1335 | 404.26 | Min Heat output(kw) |  | 327.4408
997 | 660 | 1939 | 454.55 | Min Electrical Output(kw) |  | 125.1429
1120 | 755 | 2175 | 437.09 | [14 empty] | *
1357 | 920 | 2626 | 472.83
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Plant Heat Output | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | Plant Heat Output | kWth
|  |  |  | Plant Electrical Output | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | Plant Electrical Output | kWe
|  |  |  | Plant Fuel Input | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 679 | Plant Fuel Input | kW
|  |  |  | unit cost of plant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | unit cost of plant | £/kWe

## Sheet 5
Conceptual Model -CHP Climate Change Levy Quality Analysis
| CHP 1 | CHP 2
Electricity Output (kw) | 95 | 185
Heat Output (kw) | 150 | 310
|  |  | Conversion | carbon factor | conversion
Electricity Input |  |  | Factors | kgC/kWh | to gas equiv.
Gas Input (Kw) | 310 | 620 | Electricity | 0.79 | 2.264
Running Hours | nil | 2097 | Gas | 0.21 | 1
Annual electrical Output (kw) | Nil | 387945 | Oil | 0.29 | 1.377
Annual Heat Output (Kw) |  | 650070 | Coal | 0.29 | 1.585
Annual Fuel Input (kw) |  | 1300140
Annual Electrical Efficiency % |  | 29.8387
Annual Heat Efficiency % |  | 50
Q I | Nil | 122.1774
Electricity exported to grid (kw) |  | 60115
Electricity imported from Grid |  | 4614
Cost of CC Levy( Elec Export) |  | 258.4945
CC Levy on Gas consumed (£) |  | 2600.28
CC levy on imported electricity(£) |  | 19.8402
Total cost of CC Levies (£) |  | 2878.6147
Value of levy Exemption (£) |  | 2968.3035
Net cost to client (£) | nil | -89.6888
Total costs to client per annum | 0

## Sheet 6
Conceptual Model-Effect of National insurance savings on Climate Change Levy
Annual Employers NI Contributions; Savings After 0.3 % reduction
at different salary levels in a typical organisation
|  |  | At Present |  | Post CC Levy
Average Yearly Salary | Average Monthly Salary | No. of employees | Monthly NIC per Employee | Total Yearly NIC for all Employees | Monthly NIC per Employee | Total Yearly NIC for all Employees | Saving
12500 | 1041.6667 | 5 | 82.5533 | 4953.2 | 80.5233 | 4831.4 | 121.8
15500 | 1291.6667 | 4 | 113.0533 | 5426.56 | 110.2733 | 5293.12 | 133.44
18000 | 1500 | 3 | 138.47 | 4984.92 | 135.065 | 4862.34 | 122.58
20000 | 1666.6667 | 2 | 158.8033 | 3811.28 | 154.8983 | 3717.56 | 93.72
471.54
Notes
The above calculations assume:
1. everyone pays full National Insurance Contributions (NICs)
2. there is no occupational pension scheme
3. 2000/2001 tax year